## ITP
Vendor : |  | Purchaser : | Document title: |  |  |  | Owner:
Inspection Test Plan of Clean Agent Total System
BEIJING XINDEHAO TECHNOLOGY
DEVELOPMENT Co.,Ltd
Lordegan UREA Fertilizer (1333) |  |  | Requistion no: 1333-REQ-PR-062 |  |  |  | DOC. NO. : 1333(XDH062)-ITP-06-QC-001
|  |  | Purchase Order No. : 1333-POR-PR-063 |  |  |  | Rev.1 | Page 2of 2
Activity No. | COMPONENTS | Inspection Activity and Fabrication Step&Exten of Inspection | SPECIFICATION OR PROCEDURE | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | Involved Partys
[6 empty] | V | P | TPI | O
1 | FM200 GAS FIRE EXTINGUISHING SYSTEM
1.1 | MX 200 cylinder | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
|  | Pressure test (10%) | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Test Report | H | W | W | R
1.2 | Connection hose DN 50 | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.3 | Check valve MX-CR | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.4 | Nozzles | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.5 | Release device pneumatic MX200 | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.6 | Cylinder valve | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.7 | Contact pressure gauge | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
1.8 | Pilot control manifold CO2 | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.9 | Manifold For Selector valve | Visual and dimension inspection(100%) | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | W | W | R
|  | Pressure test (100%) | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | W | W | R
1.10 | PAE CO2 EM 8 kg with reserve | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Inspection Report | H | R | R | R
1.11 | Safety device | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
1.12 | Pipe and fittings(10%) | Visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | W | W | R
2 | Control and Alarm System
2.1 | Fire alarm and control panel FMZ5000 mod 12 GAB | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
|  | Functional test of hardware(100%) | Manufacturer’s Standard Practice | manufacturer's standard practice | Test Report | H | W | W | R
2.3 | Discovery Open Area Sounder Beacon | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
2.4 | Module and terminal box | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
2.5 | Manual button | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
2.6 | visual / sounder | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
2.7 | wiring | visual and dimension inspection | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet, | Inspection Report | H | R | R | R
3 | Others
3.1 | Material certification in Factory Check for All of Material | Certification | As per Production scheduling plan and progress report | According to NFPA/EN&ASTM | Certification | H | SW | SW | R
3.2 | Packing and shipping Inspection | Packing Inspection Before Delivery | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Release Note | H | H | H | R
|  | Quality Certificate Document | As per Production scheduling plan and progress report | As per MR/Spec/Data sheet | Final Book | H | R/A | R/A | R
NOTE:
1.Legend: H = Hold Point; W = Witness Point; S. W = Witness Point on selective basis; R = Review of record / certificate; R. S = Test record to be submitted to customer; - = Not applicable; R/A=Review&Approval
V = vendor , P = Purchaser , TPI = Third Party Inspector , O = Ower/MC
2.The site test is not included in this ITP
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)