## Comment on DSH-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-91-EL-001
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | field devices detail installation drawings for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Installation details of horn to be added.
2 | Where the mini switch is installed? inside a module box or inside a detector/device? Please provide adequate detail installation and notes.
3 | Please include the wiring diagram of all devices.

## Comment on DWG-92-EL-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-92-EL-001
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | field devices detail installation drawings for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Installation details of horn to be added.
2 | Where the mini switch is installed? inside a module box or inside a detector/device? Please provide adequate detail installation and notes.
3 | Please include the wiring diagram of all devices.

## Comment on DWG-91-EL-002
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-91-EL-002
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Interconnection wiring diagram of control panel for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Title of document needs to be revised. |  | Modified
2 | Please revise based on comments on DWG-91-EL-003. |  | The monitoring module inside of CACP can monitor solenoid signal ,Please refer to the drawing of 1333(XDH062)-DWG-91-EL-005(2-2) and 1333(XDH062)-DWG-91-EL-003. |  |  | 1- Please confirm if "open status" of selector valves can be monitored by this method. Anyhow, Open status of selector valves shall be transfered to the central F&G system in Utility control room. 2-Please provide relevant connections of HFC suppression for Engineering room and Battery room.
3 | Please add refrence drawings. |  | Modified |  |  | Please indicate CACP connections of horns.
4 | [5 empty] | Please delete the pre-alarms from F&G system. Pre dicharge alarm and discharge alarms shall be provided by CACP to alarming relevant horns and lightings.

## Comment on DWG-92-EL-002
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-92-EL-002
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Interconnection wiring diagram of control panel for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Title of document needs to be revised. |  | Modified
2 | Please revise based on comments on DWG-92-EL-003. |  | The monitoring module inside of CACP can monitor solenoid signal ,Please refer to the drawing of 1333(XDH062)-DWG-92-EL-005(3-3) and 1333(XDH062)-DWG-92-EL-003. |  |  | 1- Please confirm if "open status" of selector valves can be monitored by this method. Anyhow, Open status of selector valves shall be transfered to the central F&G system in Utility control room. 2-Please provide relevant connections of HFC suppression for Engineering room and Battery room.
3 | Please add refrence drawings. |  | Modified |  |  | Please indicate CACP connections of horns.
4 | [5 empty] | Please delete the pre-alarms from F&G system. Pre dicharge alarm and discharge alarms shall be provided by CACP to alarming relevant horns and lightings.

## Comment on DWG-91-EL-003
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-91-EL-003
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Block Diagram for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Engineering room and Battery room. |  | Please see to the REF MOM NO:1333-MOM-0169,discussion 2),Battery Room and Engineer room do not need to the clean Agent To Flood system. |  |  | Please provide the relevant connections of HFC suppression for Engineering room and Battery room.
2 | Weighing switchs on PAE-EM are missed. Please indicate them. |  | The loop monitoring module(LM1/LM2) are weighing switch on PAE-EM,drawing modified |  |  | Noted.
3 | Please provide Limit switchs on selector valves of zone discharge header. Open status of it shall be available to the central F&G system. |  | Please refer to the drawing of 1333(XDH062)-DWG-91-EL-005(2-2) and 1333(XDH062)-DWG-91-EL-003. |  |  | Please confirm if "open status" of selector valves can be monitored by this method. Anyhow, Open status of selector valves shall be transfered to the central F&G system in Utility control room.
4 | Tag of module boxes to be specified. |  | Modified |  |  | Noted.
5 | Refrence drawings to be listed (Relevant P&ID). |  | Modified |  |  | Noted.
Please delete the pre-alarms from F&G system. Pre dicharge alarm and discharge alarms shall be provided by CACP to alarming relevant horns and lightings.

## Comment on DWG-92-EL-003
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-92-EL-003
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Block Diagram for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Battery room. |  | Please see to the REF MOM NO:1333-MOM-0169,discussion 2),Battery Room and Engineer room do not need to the clean Agent Total Flood system. |  |  | Please provide the relevant connections of HFC suppression for Battery room.
2 | Weighing switchs on PAE-EM are missed. Please indicate them. |  | The loop monitoring module(LM1/LM2) are weighing switch on PAE-EM,drawing modified |  |  | Noted.
3 | Please provide Limit switchs on selector valves of zone discharge header. Open status of it shall be available to the central F&G system. |  | Please refer to the drawing of 1333(XDH062)-DWG-92-EL-005(2-2) and 1333(XDH062)-DWG-92-EL-003. |  |  | Please confirm if "open status" of selector valves can be monitored by this method. Anyhow, Open status of selector valves shall be transfered to the central F&G system in Utility control room.
4 | Tag of module boxes to be specified. |  | Modified |  |  | Noted.
5 | Zone name "Control Room" to be amanded to "PDCS Room". |  | Modified |  |  | Not yet. Please do it.
6 | Refrence drawings to be listed (Relevant P&ID). |  | Modified |  |  | Noted.
7 | [5 empty] | Please delete the pre-alarms from F&G system. Pre dicharge alarm and discharge alarms shall be provided by CACP to alarming relevant horns and lightings.

## Comment on DWG-91-EL-004
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-91-EL-004
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | Control panel wiring diagram for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-91-EL-002 and DWG-91-EL-003..

## Comment on DWG-92-EL-004
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-92-EL-004
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | Control panel wiring diagram for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-92-EL-002 and DWG-92-EL-003..

## Comment on DWG-91-EL-005
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-91-EL-005
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Layout drawing of Clean Agent Control System for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-91-EL-003. |  | Engeneer room do not protected area,itwas a closed interval, and when a fire broke out, he escaped from the other gates,The sign on the gas indicator is different, and adding the indicator light and hand report may make it possible to break into the engineer station |  |  | Please revise based on comments on DWG-91-EL-003.
2 | Refrence drawings to be listed. |  | Modified |  |  | Noted.

## Comment on DWG-92-EL-005
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: |  | 1333(XDH062)-DWG-92-EL-005
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: |  | Layout drawing of Clean Agent Control System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-92-EL-003. |  | Modified |  |  | Please revise based on comments on DWG-92-EL-003.
2 | Refrence drawings to be listed. |  | Modified |  |  | Noted.

## Comment on DWG-91-EL-006
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-91-EL-006
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | Wiring of Modbox of Clean Agent Control System for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-91-EL-003.

## Comment on DWG-92-EL-006
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-015 |  |  | Document No: | 1333(XDH062)-DWG-92-EL-006
Transmittal Date: |  | 2017-09-28 |  |  | Document Title: | Wiring of Modbox of Clean Agent Control System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please revise based on comments on DWG-92-EL-003.

## Comment on DSC-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSC-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on CSH-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-CSH-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on CSH-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-CSH-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PR-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PR-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PR-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PR-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PI-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PI-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PI-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PI-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PI-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PI-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PR-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PR-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PR-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PR-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSH-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)