## cover
VENDER: |  | SUBCONTRACTOR: | LORDEGAN UREA FERTILIZER PROJECT |  |  |  | OWNER:
CONTRACTOR Consortium of AVIC&HFEC
BEIJING XINDEHAO TECHNOLOGY |  |  | COVER SHEET |  |  |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd
Project NO.: 1333 | [6 empty] | Page 1 of 18 |  |  | Rev.2
product datasheet for MX-200 system Clean Agent Total Flooding System-Item 1333-REQ-PR-062
owner:
LORDEGAN UREA FERTILIZER CO. (PUBLIC STOCK)
Project Title:
LORDEGAN UREA FERTILIZER PROJECT
Subcontractor:
Consortium of AVIC&HFEC
|  |  |  | P.O.NO.: | 1333-POR-PR-063 |  |  |  | ITEM NO.:
|  |  |  | REQ. NO.: | 1333-REQ-PR-062
|  |  |  | DOC. NO. | 1333(XDH062)-DSH-06-PR-001 |  |  |  | Rev.2
[5 empty] | NC- REVIEWED WITH NO COMMENT |  |  |  | DEPARTMENT:
[5 empty] | C-DO NOT PROCEED WITH FABRICATION |  |  |  | DATE:
[5 empty] | AC-APPROVED WITH MINOR COMMENTS |  |  |  | Person In CHARGE:
RE-DOCUMENT WAS NOT ACCEPTED
Purchaser's permission to proceed or review taken on vendor prints shall not relieve vendor form its responsibilities or liabilities under purchase order.
2 | 20/11/2017 | Issue for final |  |  |  | XH.S |  | WC.M |  | DJ.F
1 | 26/10/2017 | Issue for final |  |  |  | XH.S |  | WC.M |  | DJ.F
0 | 25/09/2017 | Issue for review |  |  |  | D.P |  | WC.M |  | DJ.F
REV. | DATE | DESCRIPTION |  |  |  | PREPARED |  | CHECKED |  | APPROVED
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## cylinder
Vendor : | SUBCONTRACTOR: |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 2 | of | 18 | Rev.2
Data Sheet for Cylinder
Product name: | Welded Steel Cylinder |  |  | Manufacturer | MINIMAX_TIANHAI
Product model | 180L 50bar |  |  | Order No.:
Product Specifications
Material |  | 4130x(30CrMo)
Working Pressure |  | 50bar
Testing Pressure |  | 1500PSI
Wall Thickness (Min.) |  | 5.9mm
Painting Color |  | RAL 3000
Weight |  | about 128kg
Length |  | about 1650mm
Operating temperature range |  | -50℃-65℃
Application Standard |  | DOT3AA-178.37
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## cylinder valve
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 3 | of | 18 | Rev.2
Data Sheet for Cylinder Valve
Product name: | Cylinder Valve |  |  | Manufacturer | MINIMAX
Product model | B0481-A DN49 |  |  | Order No.:
Product Specifications
Material |  | Steel strip EN 10048 -4,0 X60, S235JR
Operating Pressure |  | 50 bar
Weight |  | 8.9kg
Source |  | EK / Purch
Medium |  | MX200 HFC227ea
Operating temperature range |  | -20℃ up to + 50 ℃
CE conformity |  | acc. to Directive 89/106/EC
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## MX200agent
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 4 | of | 18 | Rev.2
Data Sheet for MX200 agent
Product name: | MX-200 agent |  |  | Manufacturer | MINIMAX-Waysmos
Product model | HFC 227ea |  |  | Order No.:
Product Specifications
Empirical Formula |  | CF3-CHF-CF3
Molecular weight |  | 170.03
Boiling point |  | -16.36 ℃
Freezing point |  | -131 ℃
Critical temperature |  | 101.7℃
Critical pressure |  | 2912kpa
Critical density |  | 0.6121Kg/dm3
Viscosity liquid (25℃) |  | 0.226 Cp
Vapor pressure (25℃) |  | 457.7 Kpa
Atmospheric lifetime |  | 31 - 42 years
MEC Class A |  | 5.2%( according to NFPA-2001)
NOAEL(V/V) |  | 9%
LOAEL(V/V) |  | 10.5%
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## gauge
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 5 | of | 18 | Rev.2
Data Sheet for Contact Pressure Gauge
Product name: | Contact Pressure Gauge |  |  | Manufacturer | MINIMAX
Product model | 50bar |  |  | Order No.:
Product Specifications
Tolerance ACC.to EN12094-10 |  | ± 1.3 bar
Max. prerating pressure at 50℃ |  | 60bar
pressure range |  | 45-60bar
Weight |  | 0.16kg
technical data: pressure medium ................................HFC-227ea, FK-5-1-12 nominal size .....................................................................50 accuracy class ...............................................................1,6 Operating temperature range .........................-40 °C up to +60 °C IP code ................................................IP65 with mounted cable measuring network,motion work ............................copper alloy |  |  |  | electrical data: switching voltage ................................4,5 − 24 V DC / VAC switching current ..............................................5 − 100 mA contact load .....................................max. 3 W, dry contact conducting wire ......................................two-core, 100 cm cross-section of conducting wire ..........................0.14 mm2
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Hose
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 6 | of | 18 | Rev.2
Data Sheet for Connection Hose
Product name: | Connection Hose |  |  | Manufacturer | MINIMAX
Product model | DN50 90° |  |  | Order No.:
Product Specifications
Operating medium |  | HFC - 227ea
Minimum Blending Radius |  | 630mm
Thread G1/ G2 |  | 2.1/2"-12 UNF [B1.1] / R 2." [ISO 7]
Weight |  | 6kg
Length |  | 520mm
SW1/ SW2 |  | 75/65
operating temperature range |  | -40℃ to + 60℃
working pressure |  | 80bar
test pressure |  | 120bar
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## check valve
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 7 | of | 18 | Rev.2
Data Sheet for Check Valve
Product name: | Check Valve |  |  | Manufacturer | MINIMAX
Product model | DN50 MX-CR |  |  | Order No.:
Product Specifications
Medium |  | HFC 227 ea
Operating pressure |  | 60 bar
Test pressure |  | 90 bar
Connection thread inlet / outlet |  | Rp 2 EN 10226 / Rc 2 ISO 7
Opening pressure |  | ≤3 bar
Leakage rate at 20 bar |  | ≤ 20 bubbles / 1 min
operating temperature range |  | -20°C to 60°C
Weight |  | 5.15kg
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Release device
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 8 | of | 18 | Rev.2
Data Sheet for Pneumatic Release Device
Product name: | Pneumatic Release Device |  |  | Manufacturer | MINIMAX
Product model | MX200 |  |  | Order No.:
Product Specifications
Response pressure |  | min.21 bar .max.360 bar
Weight |  | 0.48 Kg
Operating temperature range |  | - 20°C to 50°C
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Pilot Hose
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 9 | of | 18 | Rev.2
Data Sheet for Pilot Hose
Product name: | Pilot Hose |  |  | Manufacturer | MINIMAX
Product model | DN4X1000- MX200 |  |  | Order No.:
Product Specifications
Operating medium |  | HFC-227ea，nitrogen,co2
operating temperature range |  | -40 °C to +60 °C
Minimum bending radius |  | 90mm
Weight |  | 0.4kg
Operating pressure |  | 160 bar
Test pressure |  | 240 bar
Burst pressure |  | 480 bar
Notes
Lordega
UREA FERTILIZER CO. (PUBLIC STOCK)

## Safety device
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 10 | of | 18 | Rev.2
Data Sheet for Safety device malfunction pressure
Product name: | Safety device malfunction pressure |  |  | Manufacturer | MINIMAX
Product model | SFD DN4 |  |  | Order No.:
Product Specifications
Medium(for start up system) |  | nitrogen,co2
Operating pressure |  | 140 bar
Test pressure |  | 210 bar
Connection DN4 |  | Pipe 6 x 1
housing |  | Brass
Gasket |  | NBR
operating temperature range |  | -20℃ to + 50℃
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Shuttle non return valve
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 11 | of | 18 | Rev.2
Data Sheet for Shuttle non return valve
Product name: | Shuttle non return valve |  |  | Manufacturer | MINIMAX
Product model | MX-WRV DN4 6X1 |  |  | Order No.:
Product Specifications
Medium (for start up system) |  | nitrogen,co2
Operating pressure |  | 2 up to 140 bar
Test pressure |  | 210 bar
Rate of pressure rise |  | min 3 bar/s
Position of device |  | feedings only horizontal
Weight |  | 0.25kg
operating temperature range |  | -40℃ to + 60℃
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## nozzles
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 12 | of | 18 | Rev.2
Data Sheet for Nozzles
Product name: | Nozzles type CD, MX200 |  |  | Manufacturer | MINIMAX
Product model | DN 40/25/15 360° brass, 4 bore |  |  | Order No.:
Product Specifications
Medium |  | HFC-227ea with nitrogen pressure charging
Temperature range |  | -20°C to 50°C
Gradation of the bore hole ød(mm) |  | in 0,1 mm steps
ød min(mm) |  | 3±0.1
ød max(mm) |  | 16±0.1 / 10±0.1 / 5±0.1
Length |  | 85mm / 65mm / 55mm
Ød |  | 55mm / 40mm / 28mm
Weight |  | 0.6kg / 0.4kg / 0.2kg
Connection thread Rp |  | in accordance with EN 10226
operating temperature range |  | min. 9,6 bar, max. 60 bar
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## pressure switch
Vendor : |  | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY |  | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd |  | Consortium of AVIC&HFEC
PROJECT NO.: 1333 | [5 empty] | Page | 13 | of | 18 | Rev.2
Data Sheet for Pressure switch
Product name: |  | Pressure switch |  |  | Manufacturer | MINIMAX
Product model |  | G1/4" |  |  | Order No.:
Product Specifications
Agent |  |  | HFC-227ea, CO2, Ar, N2
Safe up to |  |  | 100 bar
Switching pressure falling / rising |  |  | 2 bar / 3 bar(NOTE1)
Switching tolerance |  |  | ± 0,5 bar
operating temperature range |  |  | -30 °C up to +100 °C
IP code |  |  | IP65 with plug socket
Voltage |  |  | max. 24 V
Switching current |  |  | min. 5 mA
Weight |  |  | 0,09 Kg
Notes
NOTE1: | The pressure switch will be action, when the pressure falling 2 bar or rising 3 bar. There is not set pressure
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Pilot control manifold
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 14 | of | 18 | Rev.2
Data Sheet for Pilot Control Manifold
Product name: | Pilot Control Manifold |  |  | Manufacturer | MINIMAX
Product model | DN15-2/3/4 |  |  | Order No.:
Product Specifications
Medium |  | nitrogen,co2
operating pressure |  | 60 bar
test pressure |  | 900 bar
operating temperature range |  | -20 °C up to +50 °C
Length(mm) |  | 340/490/620
Weight(kg) |  | 9.7/14.2/17.7
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Selector Valve
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 15 | of | 18 | Rev.2
Data Sheet for Selector Valve
Product name: | Selector Valve |  |  | Manufacturer | MINIMAX
Product model | MX-BV DN50/ DN80 / DN100 |  |  | Order No.:
Product Specifications
Medium |  | HFC-227ea
length of selector valve DN80 / DN100 |  | 0.37m/0.55m/0.67m
operating temperature range |  | -20 °C up to +50 °C
Test certificate manifold pipe |  | EN 10204 - 3.1
Working pressure for manifold |  | 60bar
Test pressure for manifold |  | 90bar
Working pressure for pneumatic release device |  | 20 up to 140bar
Test pressure for pneumatic release device |  | 210bar
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## safety valve
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 16 | of | 18 | Rev.2
Data Sheet for safety valve
Product name: | safety valve |  |  | Manufacturer | MINIMAX
Product model | G1/2-66 bar |  |  | Order No.:
Product Specifications
Medium(for start up system) |  | HFC-227ea
Response pressure max. |  | 66 bar at +50℃ (1)
operating temperature range |  | -20℃ to 50℃
Metal seal |  | -270℃ to +280℃
Test certificate |  | EN 10204-3.1
Position of device |  | vertical
(1) The downstream piping design pressure is no less than 160 bar
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## push button selector valve
Vendor : |  | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY |  | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd |  | Consortium of AVIC&HFEC
PROJECT NO.: 1333 | [5 empty] | Page | 17 | of | 18 | Rev.2
Data Sheet for push button selector valve
Product name: |  | push button selector valve |  |  | Manufacturer | MINIMAX
Product model |  |  |  |  | Order No.:
Product Specifications
Medium(for start up system) |  |  | co2
Operating pressure |  |  | 2 to 365 bar
operating temperature range |  |  | -20℃ to 50℃
Thread connection |  |  | for precision-drawn steel pipe 10x1
Material/ Surface | Knurled screw |  | Brass/ nickel plated
| Non-return valve |  | steel/ galvanized
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## SEP-2 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 18 | of | 26 | Rev.0
Data Sheet for main/reserve switch box
Product name: | Control device pneumatic |  |  | Manufacturer | MINIMAX
Product model | 2017-09-02 |  |  | Order No.:
Product Specifications
Medium |  | CO2
Working pressure |  | max.140bar
Thread connection |  | for precision-drawn steel pipe 6x1
Finish |  | RAL7032-pebble grey
Dimensions(WxHxD)/mm |  | 220X220X120
Limit switch | Type | ZS 256-11z
| nominal current/voltage | 4A(230VAC)/ 2.5A(400VAC)/ 1A(500VAC)
| actution force | min.9N
| Time on in percent | max.5000/h
| Operation speed | max.1m/s, min.0,01m/s
Temperature range |  | ‘-40℃ to 60℃
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## PAE
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 19 | of | 18 | Rev.2
Data Sheet for Pneumatic Release Device Electrical with Reserve
Product name: | Pneumatic release device electrical with reserve |  |  | Manufacturer | MINIMAX
Product model | PAE CO2 EM 8 kg |  |  | Order No.:
Product Specifications
Medium |  | co2
Operating pressure |  | 140bar
Test pressure |  | 210bar
Pilot cylinder volume |  | 15L
operating temperature range |  | -40℃ to 60℃
Notes
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## FM5000 MOD12 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 20 | of | 26 | Rev.0
Data Sheet for Fire alarm control panel
Product name: | Fire alarm control panel FMZ5000 MOD12 |  |  | Manufacturer | MINIMAX
Design Features
MOUNTING |  | ☑WALL □SELF STANDING □CONCRETE PAD FLOOR
DOOR |  | □HINGED RIGHT □DOOR LOCK □DEVICEHINGED LEFT
□DOUBLE HINGED ☑SINGLE DOOR
VENTILATION |  | □LOUVER ☑DOOR FRONT
PAINTIGN |  | RAL 7035
Product Parameters
Dimension |  | W 225 mm × H 604 mm × D 600 mm
Approvals |  | FM/UL/VDS
Used for |  | GAS SYSTEM
Mfr's model no. |  | FMZ5000 MOD12
Weight |  | APPROX.26KG(57.3LBS)WITHOUT MODULES
Relative humidity |  | MAX.95% NO CONDENSATION
Temperature range |  | -5℃ to +40℃（+23℉ to +104℉）
IP code |  | IP 54
Others |  | MAIN VOLTAGE AND FREQUENCY:115V/230V AC(-15%,+10%) 50-60HZ; EXTERNAL CONTROL VOLTAGE:21-29.6VDC;QUIESCENT CURRENT:120mADC
REMARKS
Medium-size base unit from the fi re alarm panel range FMZ 5000. Elegant 19" wall enclosure with front door in niro-coloured mounting. For connecting addressable detectors and conventional detectors in standard or industrial design. Activation of remote transmission units for fi re and fault signals as well as data communication to management systems and control stations with open interfaces. Signal indication through large LCD display and LEDs, menu-guided operation using confi gurable function keys.
REFERENCE DRAWING
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## MB12 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 21 | of | 26 | Rev.0
Data Sheet for Module box
Product name: | Module box MB12 |  |  | Manufacturer | MINIMAX
Design Features
MOUNTING |  | ☑WALL □SELF STANDING □CONCRETE PAD FLOOR
DOOR |  | □HINGED RIGHT □DOOR LOCK □DEVICEHINGED LEFT
□DOUBLE HINGED ☑SINGLE DOOR
Product Parameters
Dimension |  | W 500 mm × H 500 mm × D 190 mm
Used for |  | GAS SYSTEM
Mfr's model no. |  | MB12
Weight |  | 4,5KG
Relative humidity |  | MAX.95% NO CONDENSATION
Temperature range |  | -5℃ to +40℃（+23℉ to +104℉）
IP code |  | IP 54
Others |  | carbon steel
REFERENCE DRAWING
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## HZFQ-1 (hidden)
Vendor : | Contractor : |  |  | LORDEGAN UREA FERTILIZER PROJECT |  |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  |  | PRODUCT DATA SHEET |  |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 | [6 empty] | Page | 22 | of | 26 | Rev.0
Data Sheet for Gas warning light
Product name: | Gas warning light HZFQ-1 |  |  |  | Manufacturer |  | MINIMAX-KSEE
Design Features
MOUNTING |  | ☑WALL □SELF STANDING □CONCRETE PAD FLOOR
DOOR |  | □HINGED RIGHT □DOOR LOCK □DEVICEHINGED LEFT
□DOUBLE HINGED □SINGLE DOOR
Product Parameters
Dimension |  | W 300mm × H 120mm × D 26mm
Used for |  | GAS SYSTEM
Mfr's model no. |  | HZFQ-1(ENGLISH)
Relative humidity |  | MAX.95% RH40℃
Temperature range |  | -10℃ to +50℃
Text |  | type | Times New Roman |  |  | height | 1.5cm
Others |  | WORKING VOLTAGE :24±15%VDC; RATED CURRENT:≤60mA
REFERENCE DRAWING
'NOTE : ITEMS ASTERISK MARKED(*) SHALL BE FILLED IN BY VENDOR ON HIS PROPOSAL.
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## 55000-765 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 23 | of | 26 | Rev.0
Data Sheet for Input module 55000-765
Product name: | Input module 55000-765 |  |  | Manufacturer | MINIMAX-APOLLO
Design Features
MOUNTING |  | ☑WALL □SELF STANDING □CONCRETE PAD FLOOR
Product Parameters
Dimension |  | W 39 mm × H 39 mm × D 20 mm
Used for |  | GAS SYSTEM
Approvals |  | FM/UL/VDS
Mfr's model no. |  | HZFQ-1(ENGLISH)
Weight |  | APPROX.30G
Relative humidity |  | MAX.95% NO CONDENSATION
Temperature range |  | -20℃ to +70℃
Others |  | OPERATING VOLTAGE :17-28VDC; QUIESCENT CURRENT:MIN.1.25mADC MAX.3.6mADC
REMARKS
Apollo’s new Mini Switch Monitor* is a miniature interface with an entirely new housing. The unit is designed to fi t into equipment with limited space or mounted within an enclosure such as a manual call point. The interface can also be fi tted onto a standard 35mm DIN-rail using a twist-click motion*
REFERENCE DRAWING
NOTE : ITEMS ASTERISK MARKED(*) SHALL BE FILLED IN BY VENDOR ON HIS PROPOSAL.
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## SUX5000 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 24 | of | 26 | Rev.0
Data Sheet for Sux5000 AP monitoring system
Product name: | Sux5000 AP monitoring system |  |  | Manufacturer | MINIMAX
Product Parameters
Dimension |  | B 127 mm × H 125 mm × T 70 mm
Used for |  | GAS SYSTEM
Approvals |  | FM/UL/VDS
Mfr's model no. |  | SUX5000 AP
Weight |  | APPROX.4G(0.01LBS)
Relative humidity |  | MAX.93% NO CONDENSATION
Temperature range |  | -40℃ to +80℃（-40℉ to +176℉）
Others |  | OPERATING VOLTAGE :17-28VDC; OPERATING CURRENT:300μA;QUIESCENT CURRENT:230μA
REMARKS
REFERENCE DRAWING
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## Manual Auto Exchange Switch (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 25 | of | 26 | Rev.0
Data Sheet for Manual/Auto Exchange Switch
Product name: | Manual/Auto Exchange Switch |  |  | Manufacturer | MINIMAX
Product Parameters
Voltage |  | 24V
Input current alarm |  | Multi-line 15 mA
Input static current |  | Multi-line 5 mA
Environment Temperature |  | 一20～+55℃
Shell Color |  | RAL7035
IP Degree |  | IP65
REFERENCE DRAWING
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)

## DMX3000 (hidden)
Vendor : | Contractor : |  | LORDEGAN UREA FERTILIZER PROJECT |  | OWNER:
BEIJING XINDEHAO TECHNOLOGY | CONTRACTOR |  | PRODUCT DATA SHEET |  | DOC.NO.: |  | 1333(XDH062)-DSH-06-PR-001
DEVELOPMENT Co.,Ltd | Consortium of AVIC&HFEC
PROJECT NO.: 1333 |  |  |  |  | Page | 26 | of | 26 | Rev.0
Data Sheet for Water-proof manual release/delay/abort button DMX3000
Product name: | Sounder 58000-011 |  |  | Manufacturer | MINIMAX
Design Features
MOUNTING |  | ☑WALL □SELF STANDING □CONCRETE PAD FLOOR
Product Parameters
Dimension |  | W 125 mm × H 125mm × D 32.5 mm
Used for |  | GAS SYSTEM
Approvals |  | FM/UL/VDS
Mfr's model no. |  | DMX3000
Weight |  | APPROX.500G
Environment temperature |  | -30℃ to +70℃
IP code |  | IP42
Others |  | OPERATING VOLTAGE :7.6-13.2VDC; QUIESCENT CURRENT:5mA ALARM CURRENT:20mA
BOX
REMARKS
Applicable alarm for operation on conventional lines of the fire alarm panels FMZ5000. The printed symbol (burning house) and the white inside panel comply with EN 54-11. The white inside sign can be replaced with other labels. Markings or labels which do not comply with the standard will void the VdS and EN 54-11 approvals. Operating instructions is included with the detector. The three types button have different founction,the structure inside are different, the manual release and delay button are self keep type, can reset it use reset switch inside, and the manual abort button is self reset type, that means you must keep pushing down the button, and lift finger to reset.
REFERENCE DRAWING
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)