## catalogue
Vendor : |  | Contractor : |  | Owner:
Comment
Requisition subject: Clean Agent Total Flooding System |  |  |  | Doc. Comment on 1333(XDH062)
Engineering:NON-Engineering
Srl. | Document Number | Rev.No | DOCUMENT TITLE | Sheet No. | Status | Remark
Vendor project document no.
1899-12-31 | Engineering
1899-12-31 02:24 | PROCESS
1.1.1 | 1333(XDH062)-DSH-06-PR-001 |  | Product Data Sheet for MX-200 system | Comment on DSH-06-PR-001'!A1
1.1.2 | 1333(XDH062)-MNL-06-PR-001 |  | Manuals for MX-200 system (include installation/maintenance/operation manuals) | Comment on MNL-06-PR-001'!A1
1.1.3 | 1333(XDH062)-LST-91-PR-001 |  | All_ZoneList for Utility Control Room | Comment on LST-91-PR-001'!A1 | No Comment
1.1.4 | 1333(XDH062)-LST-92-PR-001 |  | All_ZoneList for Utility Substation | Comment on LST-92-PR-001'!A1 | No Comment
1.1.5 | 1333(XDH062)-DSC-91-PR-001 |  | MX200 System Design Description for Utility Control Room | Comment on DSC-91-PR-001'!A1
1.1.6 | 1333(XDH062)-DSC-92-PR-001 |  | MX200 System Design Description for Utility Substation | Comment on DSC-92-PR-001'!A1
1.1.7 | 1333(XDH062)-CSH-91-PR-001 |  | MX200 System Calculation Datasheet for Utility Control Room | Comment on CSH-91-PR-001'!A1
1.1.8 | 1333(XDH062)-CSH-92-PR-001 |  | MX200 System Calculation Datasheet for Utility Substation | Comment on CSH-92-PR-001 '!A1
1.1.9 | 1333(XDH062)-MTO-91-PR-001 |  | MX200 System Material List for Utility Control Room | Comment on MTO-91-PR-001'!A1
1.1.10 | 1333(XDH062)-MTO-92-PR-001 |  | MX200 System Material List for Utility Substation | Comment on MTO-92-PR-001'!A1
1.1.11 | 1333(XDH062)-PID-91-PR-001 |  | MX200 System P&I Drawing for Utility Control Room | Comment on PID-91-PR-001'!A1 | No Comment
1.1.12 | 1333(XDH062)-PID-92-PR-001 |  | MX200 System P&I Drawing for Utility Substation | Comment on PID-92-PR-001'!A1 | No Comment
1.1.13 | 1333(XDH062)-DWG-91-PR-001 |  | Legend of Stationary MX200 System for Utility Control Room | Comment on DWG-91-PR-001'!A1 | No Comment
1.1.14 | 1333(XDH062)-DWG-92-PR-001 |  | Legend of Stationary MX200 System for Utility Substation | Comment on DWG-92-PR-001'!A1 | No Comment
1.1.15 | 1333(XDH062)-DWG-91-PR-002 |  | The Layout Drawing of MX200 System Storage Cylinders for Utility Control Room | Comment on DWG-91-PR-002'!A1
1.1.16 | 1333(XDH062)-DWG-92-PR-002 |  | The Layout Drawing of MX200 System Storage Cylinders for Utility Substation | Comment on DWG-92-PR-002'!A1
1.1.17 | 1333(XDH062)-DWG-91-PI-001 |  | Layout Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PI-001'!A1
1.1.18 | 1333(XDH062)-DWG-92-PI-001 |  | Layout Drawing of MX200 System for Utility Substation | Comment on DWG-92-PI-001'!A1
1.1.19 | 1333(XDH062)-DWG-91-PI-002 |  | Isometric Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PI-002'!A1
1.1.20 | 1333(XDH062)-DWG-92-PI-002 |  | Isometric Drawing of MX200 System for Utility Substation | Comment on DWG-92-PI-002'!A1
1.1.21 | 1333(XDH062)-DWG-91-PR-003 |  | Pipe Support & Hanger Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PR-003'!A1
1.1.22 | 1333(XDH062)-DWG-92-PR-003 |  | Pipe Support & Hanger Drawing of MX200 System for Utility Substation | Comment on DWG-92-PR-003'!A1
1899-12-31 04:48 | ELECTRICAL
1.2.1 | 1333(XDH062)-DSH-06-IN-001 |  | Product Data Sheet for Clean Agent Control System | Comment on DSH-06-IN-001'!A1
1.2.2 | 1333(XDH062)-MNL-06-IN-001 |  | Manuals for Clean Agent Control System (include installation/maintenance/operation manuals) | Comment on MNL-06-IN-001'!A1
1.2.3 | 1333(XDH062)-LST-91-IN-001 |  | I/O list for Utility Control Room | Comment on LST-91-IN-001'!A1
1.2.4 | 1333(XDH062)-LST-92-IN-001 |  | I/O list for Utility Substation | Comment on LST-92-IN-001'!A1
1.2.5 | 1333(XDH062)-DWG-91-EL-001 |  | field devices detail installation drawings for Utility Control Room | Comment on DWG-91-EL-001'!A1
1.2.6 | 1333(XDH062)-DWG-92-EL-001 |  | field devices detail installation drawings for Utility Substation | Comment on DWG-92-EL-001'!A1
1.2.7 | 1333(XDH062)-DWG-91-EL-002 |  | Interconnection wiring diagram of control panel for Utility Control Room | Comment on DWG-91-EL-002'!A1
1.2.8 | 1333(XDH062)-DWG-92-EL-002 |  | Interconnection wiring diagram of control panel for Utility Substation | Comment on DWG-92-EL-002'!A1
1.2.9 | 1333(XDH062)-DWG-91-EL-003 |  | Block Diagram for Utility Control Room | Comment on DWG-91-EL-003'!A1
1.2.10 | 1333(XDH062)-DWG-92-EL-003 |  | Block Diagram for Utility Substation | Comment on DWG-92-EL-003'!A1
1.2.11 | 1333(XDH062)-DWG-91-EL-004 |  | Control panel wiring diagram for Utility Control Room | Comment on DWG-91-EL-004'!A1
1.2.12 | 1333(XDH062)-DWG-92-EL-004 |  | Control panel wiring diagram for Utility Substation | Comment on DWG-92-EL-004'!A1
1.2.13 | 1333(XDH062)-DWG-91-EL-005 |  | Layout drawing of Clean Agent Control System for Utility Control Room | Comment on DWG-91-EL-005'!A1
1.2.14 | 1333(XDH062)-DWG-92-EL-005 |  | Layout drawing of Clean Agent Control System for Utility Substation | Comment on DWG-92-EL-005'!A1
1.2.15 | 1333(XDH062)-DWG-91-EL-006 |  | Wiring of Modbox of Clean Agent Control System for Utility Control Room | Comment on DWG-91-EL-006'!A1
1.2.16 | 1333(XDH062)-DWG-92-EL-006 |  | Wiring of Modbox of Clean Agent Control System for Utility Substation | Comment on DWG-92-EL-006'!A1
1.2.17 | 1333(XDH062)-LST-91-EL-001 |  | Cable List for Utility Control Room | Comment on LST-91-EL-001'!A1
1.2.18 | 1333(XDH062)-LST-92-EL-001 |  | Cable List for Utility Substation | Comment on LST-92-EL-001'!A1
1.2.19 | 1333(XDH062)-LST-91-IN-002 |  | Cause & Effective Table for Utility Control Room | Comment on LST-91-IN-002'!A1
1.2.20 | 1333(XDH062)-LST-92-IN-002 |  | Cause & Effective Table for Utility Substation | Comment on LST-92-IN-002'!A1
1.2.21 | 1333(XDH062)-MTO-91-EL-001 |  | Material List of Clean Agent Control System for Utility Control Room | Comment on MTO-91-EL-001'!A1
1.2.22 | 1333(XDH062)-MTO-92-EL-002 |  | Material List of Clean Agent Control System for Utility Substation | Comment on MTO-92-EL-002'!A1
1.2.23 | 1333(XDH062)-BOM-91-EL-001 |  | control panel bill of material for Utility Control Room | Comment on BOM-91-EL-001'!A1
1.2.24 | 1333(XDH062)-BOM-92-EL-002 |  | control panel bill of material for Utility Substation | Comment on BOM-92-EL-002'!A1
1900-01-01 | NON-Engineering
1900-01-01 02:24 | 1333(XDH062)-DLT-06-DC-001 |  | Vendor Document Index of Clean Agent Total System
1900-01-01 04:48 | 1333(XDH062)-ITP-06-QC-001 |  | Inspection Test Plan of Clean Agent Total System
1900-01-01 07:12 | 1333(XDH062)-RPT-06-QA-001 |  | Quality Documents ( factory certification or/and type inspection or/and certificate)
1900-01-01 09:36 | 1333(XDH062)-DLT-06-PJ-001 |  | Final book index
1900-01-01 12:00 | 1333(XDH062)-DLT-06-PQ-001 |  | Certificate of Origin
1900-01-01 14:24 | 1333(XDH062)-LST-06-PQ-001 |  | Master Packing List
1900-01-01 16:48 | 1333(XDH062)-LST-06-PQ-002 |  | Detail Packing List
1900-01-01 19:12 | 1333(XDH062)-LST-06-PJ-003 |  | Two Years Spare Parts List
total
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
请直接点击超链接在相应文件下添加意见，在状态栏中选择“Comment”"No Comment",如有其它意见请在备注栏中标注。
注：为简单方便查询，未提交的处在隐藏状态！！

## Comment on DSH-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## 1333(XDH062)-DWG-91-PI-001 (hidden)
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-019 |  |  | Document No: | 1333(XDH062)-DWG-91-PI-001
Transmittal Date: |  | 2017-10-13 |  |  | Document Title: | Layout Drawing of MX200 System for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | Please turn the colour of dimension and note into black on the white background. |  | Has been corrected
1900-01-01

## Comment on DSC-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSC-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## 1333(XDH062)-LST-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-LST-92-PR-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | All_ZoneList for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
no comments

## 1333(XDH062)-DSC-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-DSC-92-PR-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | MX200 System Design Description for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
Please turn the colour of dimension and note into black on the white background..And make the drawing frame completed.

## Comment on CSH-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-CSH-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## 1333(XDH062)-PID-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-PID-92-PR-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | MX200 System P&I Drawing for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
no comments

## Comment on CSH-91-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-CSH-91-PR-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | MX200 System Calculation Datasheet for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
Please recalculate if your piping layout changed has a effect on the calculate result.

## Comment on DWG-91-PI-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-DWG-91-PI-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | Layout Drawing of MX200 System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | Please recheck your piping layout because your piping on the second floor have clashed with our HVAC pipings.And our HVAC pipings have been constructed on site so we suggest that you'd better keep your pipings bottom elevation above 7.98m，or keep your pipings top elevation below 6.67m.And please note that if you move your pipe in the west part to the upside of our HVAC pipe ,your pipe may be too close to the roof beam. Detail please refer to attachment drawings.
1900-01-01

## Comment on DWG-92-PI-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PI-002
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-DWG-91-PI-002
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | Isometric Drawing of MX200 System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | Please recheck your piping layout because your piping on the second floor have clashed with our HVAC pipings.And our HVAC pipings have been constructed on site so we suggest that you'd better keep your pipings bottom elevation above 7.98m，or keep your pipings top elevation below 6.67m.And please note that if you move your pipe in the west part to the upside of our HVAC pipe ,your pipe may be too close to the roof beam. Detail please refer to attachment drawings.
1900-01-01

## Comment on DWG-91-PI-003
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: |  | 1333(XDH062)-DWG-91-PI-003
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: |  | The Layout Drawing of MX200 System Storage Cylinders for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | Please turn the colour of dimension and note into black on the white background. |  | Has been corrected |  |  | no comments

## Comment on DWG-92-PI-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-DWG-91-PR-001
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | Legend of Stationary MX200 System for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
no comments

## Comment on DWG-92-PR-002
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-027 |  |  | Document No: | 1333(XDH062)-DWG-92-PR-002
Transmittal Date: |  | 2017-12-08 |  |  | Document Title: | Pipe Support & Hanger Drawing of MX200 System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
no comments

## Comment on DWG-92-PR-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PR-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSH-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## 1333(XDH062)-DWG-91-PI-002 (hidden)
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-019 |  |  | Document No: | 1333(XDH062)-DWG-91-PI-002
Transmittal Date: |  | 2017-10-13 |  |  | Document Title: | Isometric Drawing of MX200 System for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | See attachment |  | modified
1900-01-01 | Please turn the colour of dimension and note into black on the white background. |  | Has been corrected

## 1333(XDH062)-DWG-91-PI-003 (hidden)
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-019 |  |  | Document No: | 1333(XDH062)-DWG-91-PI-003
Transmittal Date: |  | 2017-10-13 |  |  | Document Title: | The Layout Drawing of MX200 System Storage Cylinders for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1899-12-31 | Please turn the colour of dimension and note into black on the white background. |  | Has been corrected

## 1333(XDH062)-CSH-91-PR-001 (hidden)
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-009 |  |  | Document No: | 1333(XDH062)-CSH-91-PR-001
Transmittal Date: |  | 2017-10-12 |  |  | Document Title: | MX200 System Calculation Datasheet for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
no comments