## catalogue
Vendor : |  | Contractor : |  | Owner:
Comment
Requisition subject: Clean Agent Total Flooding System |  |  |  | Doc. Comment on 1333(XDH062)
Engineering:NON-Engineering
Srl. | Document Number | Rev.No | DOCUMENT TITLE | Sheet No. | Status | Remark
Vendor project document no.
1 | Engineering
1.1 | PROCESS
1.1.1 | 1333(XDH062)-DSH-06-PR-001 |  | Product Data Sheet for MX-200 system | Comment on DSH-06-PR-001'!A1
1.1.2 | 1333(XDH062)-MNL-06-PR-001 |  | Manuals for MX-200 system (include installation/maintenance/operation manuals) | Comment on MNL-06-PR-001'!A1
1.1.3 | 1333(XDH062)-LST-91-PR-001 |  | All_ZoneList for Utility Control Room | Comment on LST-91-PR-001'!A1 | No Comment
1.1.4 | 1333(XDH062)-LST-92-PR-001 |  | All_ZoneList for Utility Substation | Comment on LST-92-PR-001'!A1 | No Comment
1.1.5 | 1333(XDH062)-DSC-91-PR-001 |  | MX200 System Design Description for Utility Control Room | Comment on DSC-91-PR-001'!A1
1.1.6 | 1333(XDH062)-DSC-92-PR-001 |  | MX200 System Design Description for Utility Substation | Comment on DSC-92-PR-001'!A1
1.1.7 | 1333(XDH062)-CSH-91-PR-001 |  | MX200 System Calculation Datasheet for Utility Control Room | Comment on CSH-91-PR-001'!A1
1.1.8 | 1333(XDH062)-CSH-92-PR-001 |  | MX200 System Calculation Datasheet for Utility Substation | Comment on CSH-92-PR-001 '!A1
1.1.9 | 1333(XDH062)-MTO-91-PR-001 |  | MX200 System Material List for Utility Control Room | Comment on MTO-91-PR-001'!A1
1.1.10 | 1333(XDH062)-MTO-92-PR-001 |  | MX200 System Material List for Utility Substation | Comment on MTO-92-PR-001'!A1
1.1.11 | 1333(XDH062)-PID-91-PR-001 |  | MX200 System P&I Drawing for Utility Control Room | Comment on PID-91-PR-001'!A1 | No Comment
1.1.12 | 1333(XDH062)-PID-92-PR-001 |  | MX200 System P&I Drawing for Utility Substation | Comment on PID-92-PR-001'!A1 | No Comment
1.1.13 | 1333(XDH062)-DWG-91-PR-001 |  | Legend of Stationary MX200 System for Utility Control Room | Comment on DWG-91-PR-001'!A1 | No Comment
1.1.14 | 1333(XDH062)-DWG-92-PR-001 |  | Legend of Stationary MX200 System for Utility Substation | Comment on DWG-92-PR-001'!A1 | No Comment
1.1.15 | 1333(XDH062)-DWG-91-PR-002 |  | The Layout Drawing of MX200 System Storage Cylinders for Utility Control Room | Comment on DWG-91-PR-002'!A1
1.1.16 | 1333(XDH062)-DWG-92-PR-002 |  | The Layout Drawing of MX200 System Storage Cylinders for Utility Substation | Comment on DWG-92-PR-002'!A1
1.1.17 | 1333(XDH062)-DWG-91-PI-001 |  | Layout Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PI-001'!A1
1.1.18 | 1333(XDH062)-DWG-92-PI-001 |  | Layout Drawing of MX200 System for Utility Substation | Comment on DWG-92-PI-001'!A1
1.1.19 | 1333(XDH062)-DWG-91-PI-002 |  | Isometric Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PI-002'!A1
1.1.20 | 1333(XDH062)-DWG-92-PI-002 |  | Isometric Drawing of MX200 System for Utility Substation | Comment on DWG-92-PI-002'!A1
1.1.21 | 1333(XDH062)-DWG-91-PR-003 |  | Pipe Support & Hanger Drawing of MX200 System for Utility Control Room | Comment on DWG-91-PR-003'!A1
1.1.22 | 1333(XDH062)-DWG-92-PR-003 |  | Pipe Support & Hanger Drawing of MX200 System for Utility Substation | Comment on DWG-92-PR-003'!A1
1.2 | ELECTRICAL
1.2.1 | 1333(XDH062)-DSH-06-IN-001 |  | Product Data Sheet for Clean Agent Control System | Comment on DSH-06-IN-001'!A1
1.2.2 | 1333(XDH062)-MNL-06-IN-001 |  | Manuals for Clean Agent Control System (include installation/maintenance/operation manuals) | Comment on MNL-06-IN-001'!A1
1.2.3 | 1333(XDH062)-LST-91-IN-001 |  | I/O list for Utility Control Room | Comment on LST-91-IN-001'!A1
1.2.4 | 1333(XDH062)-LST-92-IN-001 |  | I/O list for Utility Substation | Comment on LST-92-IN-001'!A1
1.2.5 | 1333(XDH062)-DWG-91-EL-001 |  | field devices detail installation drawings for Utility Control Room | Comment on DWG-91-EL-001'!A1
1.2.6 | 1333(XDH062)-DWG-92-EL-001 |  | field devices detail installation drawings for Utility Substation | Comment on DWG-92-EL-001'!A1
1.2.7 | 1333(XDH062)-DWG-91-EL-002 |  | Interconnection wiring diagram of control panel for Utility Control Room | Comment on DWG-91-EL-002'!A1
1.2.8 | 1333(XDH062)-DWG-92-EL-002 |  | Interconnection wiring diagram of control panel for Utility Substation | Comment on DWG-92-EL-002'!A1
1.2.9 | 1333(XDH062)-DWG-91-EL-003 |  | Block Diagram for Utility Control Room | Comment on DWG-91-EL-003'!A1
1.2.10 | 1333(XDH062)-DWG-92-EL-003 |  | Block Diagram for Utility Substation | Comment on DWG-92-EL-003'!A1
1.2.11 | 1333(XDH062)-DWG-91-EL-004 |  | Control panel wiring diagram for Utility Control Room | Comment on DWG-91-EL-004'!A1
1.2.12 | 1333(XDH062)-DWG-92-EL-004 |  | Control panel wiring diagram for Utility Substation | Comment on DWG-92-EL-004'!A1
1.2.13 | 1333(XDH062)-DWG-91-EL-005 |  | Layout drawing of Clean Agent Control System for Utility Control Room | Comment on DWG-91-EL-005'!A1
1.2.14 | 1333(XDH062)-DWG-92-EL-005 |  | Layout drawing of Clean Agent Control System for Utility Substation | Comment on DWG-92-EL-005'!A1
1.2.15 | 1333(XDH062)-DWG-91-EL-006 |  | Wiring of Modbox of Clean Agent Control System for Utility Control Room | Comment on DWG-91-EL-006'!A1
1.2.16 | 1333(XDH062)-DWG-92-EL-006 |  | Wiring of Modbox of Clean Agent Control System for Utility Substation | Comment on DWG-92-EL-006'!A1
1.2.17 | 1333(XDH062)-LST-91-EL-001 |  | Cable List for Utility Control Room | Comment on LST-91-EL-001'!A1
1.2.18 | 1333(XDH062)-LST-92-EL-001 |  | Cable List for Utility Substation | Comment on LST-92-EL-001'!A1
1.2.19 | 1333(XDH062)-LST-91-IN-002 |  | Cause & Effective Table for Utility Control Room | Comment on LST-91-IN-002'!A1
1.2.20 | 1333(XDH062)-LST-92-IN-002 |  | Cause & Effective Table for Utility Substation | Comment on LST-92-IN-002'!A1
1.2.21 | 1333(XDH062)-MTO-91-EL-001 |  | Material List of Clean Agent Control System for Utility Control Room | Comment on MTO-91-EL-001'!A1
1.2.22 | 1333(XDH062)-MTO-92-EL-002 |  | Material List of Clean Agent Control System for Utility Substation | Comment on MTO-92-EL-002'!A1
1.2.23 | 1333(XDH062)-BOM-91-EL-001 |  | control panel bill of material for Utility Control Room | Comment on BOM-91-EL-001'!A1
1.2.24 | 1333(XDH062)-BOM-92-EL-002 |  | control panel bill of material for Utility Substation | Comment on BOM-92-EL-002'!A1
2 | NON-Engineering
2.1 | 1333(XDH062)-DLT-06-DC-001 |  | Vendor Document Index of Clean Agent Total System
2.2 | 1333(XDH062)-ITP-06-QC-001 |  | Inspection Test Plan of Clean Agent Total System
2.3 | 1333(XDH062)-RPT-06-QA-001 |  | Quality Documents ( factory certification or/and type inspection or/and certificate)
2.4 | 1333(XDH062)-DLT-06-PJ-001 |  | Final book index
2.5 | 1333(XDH062)-DLT-06-PQ-001 |  | Certificate of Origin
2.6 | 1333(XDH062)-LST-06-PQ-001 |  | Master Packing List
2.7 | 1333(XDH062)-LST-06-PQ-002 |  | Detail Packing List
2.8 | 1333(XDH062)-LST-06-PJ-003 |  | Two Years Spare Parts List
total
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
I.C.O.F.C
Lordegan
UREA FERTILIZER CO. (PUBLIC STOCK)
请直接点击超链接在相应文件下添加意见，在状态栏中选择“Comment”"No Comment",如有其它意见请在备注栏中标注。
注：为简单方便查询，未提交的处在隐藏状态！！

## Comment on DSH-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-LST-91-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | All_ZoneList for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Engineering room and Battery room. |  | The Engineering room and the Battery room do not need the HFC suppression according to the 1333-MOM-0169, please recheck and confirm it |  |  | It is a normal practice to keep the same concepts in design of one project. Minimax shall keep the same approch as applied in "Process Area", for buildings of Utility Area.

## Comment on LST-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-LST-92-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | All_ZoneList for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Engineering room and Battery room. |  | The Engineering room and the Battery room do not need the HFC suppression according to the 1333-MOM-0169, please recheck and confirm it |  |  | It is a normal practice to keep the same concepts in design of one project. Minimax shall keep the same approch as applied in "Process Area", for buildings of Utility Area.

## Comment on DSC-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSC-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSC-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on CSH-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-CSH-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on CSH-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-CSH-92-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-PR-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-PR-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on PID-91-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-PID-91-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | MX200 System P&I Drawing for Utility Control Room
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Engineering room and Battery room. |  | The Engineering room and the Battery room do not need the HFC suppression according to the 1333-MOM-0169, please recheck and confirm it |  |  | It is a normal practice to keep the same concepts in design of one project. Minimax shall keep the same approch as applied in "Process Area", for buildings of Utility Area.
2 | Weighing switchs on PAE-EM are missed. Please indicate them. |  | The weighing switch on the PAE-EM is present and has been marked with a cloud line in the figure. |  |  | Noted.
3 | Please provide Limit switchs on selector valves of zone discharge header. Open status of it shall be available on the central F&G system. |  | There is no limit switch on the selector valves, but its status can be show by pressure switch. And this signal will be transformed to the F&G system |  |  | If a selector valve left open (after an activation or by fault…), discharge of gas to another protected room will not reach to a design concentration and no successful fire suppression. So open status of selector valve shall be available on the central F&G system to avoid unwanted discharge of gas to the another protected room.
4 | Refrence drawings to be listed (Zone List). |  | modified |  |  | Noted.

## Comment on PID-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-PID-92-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | MX200 System P&I Drawing for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Please provide HFC suppression for Engineering room and Battery room. |  | The Engineering room and the Battery room do not need the HFC suppression according to the 1333-MOM-0169, please recheck and confirm it |  |  | It is a normal practice to keep the same concepts in design of one project. Minimax shall keep the same approch as applied in "Process Area", for buildings of Utility Area.
2 | Weighing switchs on PAE-EM are missed. Please indicate them. |  | The weighing switch on the PAE-EM is present and has been marked with a cloud line in the figure. |  |  | Noted.
3 | Please provide Limit switchs on selector valves of zone discharge header. Open status of it shall be available on the central F&G system. |  | There is no limit switch on the selector valves, but its status can be show by pressure switch. And this signal will be transformed to the F&G system |  |  | If a selector valve left open (after an activation or by fault…), discharge of gas to another protected room will not reach to a design concentration and no successful fire suppression. So open status of selector valve shall be available on the central F&G system to avoid unwanted discharge of gas to the another protected room.
4 | Refrence drawings to be listed (Zone List). |  | modified |  |  | Noted.

## Comment on DWG-91-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-DWG-91-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | MX200 System P&I Drawing for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Symbol of some devices (e.g. fire horn) is missed. Please recheck the relevant documents and provide a complete Symbol & Legneds. |  | modified |  |  | Noted.
2 | Symbol of A/M is not match with the indicated one in P&ID, Block Diagram... Please recheck the relevant documents and provide a unique Symbol & Legneds in all of them. |  | modified |  |  | Noted.

## Comment on DWG-92-PR-001
|  |  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  |  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  | 1333(XDH062)-AH-TR-012 |  |  | Document No: |  | 1333(XDH062)-DWG-92-PR-001
Transmittal Date: |  | 2017-09-21 |  |  | Document Title: |  | Legend of Stationary MX200 System for Utility Substation
No | Comment By HFEC |  | Reply by Vendor(date)
1 | Symbol of some devices (e.g. fire horn) is missed. Please recheck the relevant documents and provide a complete Symbol & Legneds. |  | modified |  |  | Noted.
2 | Symbol of A/M is not match with the indicated one in P&ID, Block Diagram... Please recheck the relevant documents and provide a unique Symbol & Legneds in all of them. |  | modified |  |  | Noted.

## Comment on DWG-91-PR-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PR-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PR-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PR-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PI-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PI-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PI-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PI-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PI-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PI-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PI-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-PR-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-PR-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-PR-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-PR-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DSH-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DSH-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MNL-06-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MNL-06-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-003 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-003
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-004 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-004
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-005 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-005
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-91-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-91-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on DWG-92-EL-006 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-DWG-92-EL-006
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-91-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-91-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on LST-92-IN-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-LST-92-IN-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on MTO-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-MTO-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-91-EL-001 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-91-EL-001
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)

## Comment on BOM-92-EL-002 (hidden)
|  | Lordegan Urea Fertilizer Project Comment Sheet |  |  |  | OWNER:
Lordegan Urea fertilizer Co. (Poblic stocks)
|  | Project No. 1333 | Responder: | Issue Date:
Reply to Transmittal No. : |  |  |  | Document No: | 1333(XDH062)-BOM-92-EL-002
Transmittal Date: |  |  |  | Document Title: | Vendor Document Control Index of MX200 and Control System
No | Comment By HFEC | Reply by Vendor(date)